Module 1: Electrical Raceways 🔑 Answer Key 1.2: Conduit Installation Principles

Instructor Reference — Self-Check 1.2 Answers

| # | Answer | Explanation |
| --- | --- | --- |
| 1 | C | 360° — equivalent to four 90° bends between pull points. |
| 2 | C | A dashed line represents conduit run underground or under the floor. |
| 3 | A | The standard take-up for 1/2" EMT is 5 inches (12.7 cm). |
| 4 | B | Reaming removes sharp burrs that can slice through wire insulation. |
| 5 | B | The multiplier for a 30° offset bend is 2.0. |
| 6 | B | Conduit must be supported within 0.9 meters (3 feet) of every outlet box or fitting. |
| 7 | C | A plumb bob or spirit level ensures vertical conduit runs are perfectly straight. |
| 8 | C | The conduit "shrinks" (gets shorter) due to the angled travel in an offset bend. |
| 9 | C | The Schedule of Loads contains conduit size, wire size, and breaker ratings. |
| 10 | B | A kinked or flattened bend is a code violation and makes wire pulling difficult or impossible. |

— End of Answer Key 1.2 —